## Slide 1: Evolution and Improvements of Air Filtration
Brant Oldewage CAFS
Flanders Corporation
ASHME May 2, 2014

## Slide 2: Filtration Firsts
LEWIS HASLETT: Lung Mask
First form of air filtration?
Fire departments were among the first to use “gas masks” and the first one to receive an American patent was an “Inhaler or Lung Mask” by Lewis Haslett of Louisville, Kentucky, in 1849.
Mr. Haslett’s device utilized a filter of wool or other porous material moistened with water to filter out particles.

## Slide 3: Asbestos and Glass Media Filtration
Introduction of the disposable glass (wool) fiber for air filter material.
Owens-Corning 1934
Asbestos used thru 1960’s
Fiberglass filtration evolved

## Slide 4: Evolution of the HEPA filter
1940s-1950s: US Atomic Energy Commission had a need for filtering and the containment of radioactive aerosols.
This top classified project was due to the development of the Atomic Bomb.
Later named “The Manhattan Project”
Originally called the “super impingement” filter and or “Absolute”, then the name of HEPA filter agreed upon for High Efficiency Particulate Air.
First Producers: Flanders, Cambridge, and Mine Safety Appliances.

## Slide 5: HEPA Filter History

## Slide 6: Evolution of the HEPA filter
1950s: Glass fibers were introduced into the filter media
1960s: Specifications were standardized and called HEPA filters
1970s: Asbestos was removed
Today: Micro-fine glass media strands still used.
Efficiency levels from 99.97% @ .3 micrometer up to 99.9995% on .12 micrometer size particles (ULPA) Ultra Low Penetrating Air
Separator and separatorless media packs

## Slide 7: Evolution of the HEPA filter
High Capacity HEPA filters for higher flow rates, offering a lower initial PD.
High Temp HEPA filters with requirements up to 1000 degrees F for exhaust and 500 degrees for supply air.
High Velocity – Low Resistance HEPA filters: utilized where high air flow applications and ultra low pressure drop are required.

## Slide 8: Evolution of HEPA Filters
A
i
r
f
l
o
w

## Slide 9: Basic – Medium Filtration Advancements from 1960’s thru today
Hogs Hair, Rolls, and Panels to Pleated filters.
Pleated filters originally produced with blends of cotton media rather than glass.
Offered higher Dust Holding Capacities.
Increased efficiencies
Increased surface area

## Slide 10: Basic – Medium Filtration: Advancements from 1960’s thru today
Polyester Synthetic Media as an alternative to Glass
Efficiencies due to media types and blends increased from 20%+ to 90%+
Bag / Pocket filters: Increased surface area, ease of installation
Rigid Box Filters: Media contained in a rigid box style filter.

## Slide 11: Basic – Medium Filtration: Advancements from 1960’s thru today
Extended Surface Mini Pleat products with surface area exceeding 200 s/f.
Initial Resistance (PD) clean @.25” in a 24x24x12 4-V configuration.
Synthetic Media options in 2”, 4”, 6”, and 12” media packs with plastic frames.

## Slide 12: Basic – Medium Filtration: Advancements from 1960’s thru today
BENEFITS
Increased Surface Area (pleated and mini pleated)
Lower initial resistance
Higher Dust Holding Capacity
Synthetic Medias
Energy Savings Products
labor cost savings and disposal cost savings
As the need for filtration improved, so did the requirements for a standardization of the efficiencies and product classifications.

## Slide 13: ASHRAE 52.1 to 52.2 History
NBS Dust Spot Test (from 1940’s) Intended to be an indication of removal of staining particles.
HEPA paper targets placed upstream & downstream of test filter
Ambient atmospheric air challenge
Adopted by ASHRAE 1968 into ASHRAE Standard 52
Revised in 1976 into ASHRAE 52-76
Revised in 1992 into ASHRAE 52.1-1992
ASHRAE 52.2 started in 1992
The introduction of MERV: Minimum Efficiency Reporting Value

## Slide 14: ASHRAE 52.1 to 52.2 History
ASHRAE 52.2-1999 Particle size efficiency test method
ASHRAE 52.2-2007 minor rewrite
ASHRAE 52.2-2007 B published in 2008
Added DHC Dust Holding Capacity and Arrestance.
Allowed for the withdrawal of ASHRAE 52.1-1992

## Slide 15: ASHRAE 52.1 to 52.2 History
ASHRAE 52.2 Appendix J Added 2008
Conditioning step for the 52.2 standard
Method of identification of the drop in filter efficiency.
The reported value per Appendix J would be referred to as MERV ‘A.’
Filters tested per Standard 52.2 with Appendix J option would have both MERV and a MERV ‘A’ reported value.

## Slide 17: MERV chart with 52.2 and 52.1

## Slide 18: ASHRAE Standards and Guidelines continue to develop and improve

## Slide 20: ANSI /ASHRAE /ASHE Standard 170-2008 Table 6-1 Minimum Filter Efficiencies
Space Designation (According to Function) | Filter Bank Number 1 (MERV)a | Filter Bank Number 2 (MERV)a
Classes B and C Surgery, inpatient and ambulatory diagnostic and therapeutic radiology, inpatient delivery and recovery services | 7 | 14
In patient care, treatment, and diagnosis, and those spaces providing direct service or clean supplies and clean processing (except as noted below); AII rooms | 7 | 14
Protective environment (PE) rooms | 7 | (HEPA)c,d
Laboratories; class A surgery and associated semi-restricted spaces | 13b | N/R*
* NR= not required Note a: The minimum efficiency reporting value (MERV) is based on the method of testing described in ANSI/ASHRAE Standard 52.2-2007, Method of Testing General Ventilation Air-Cleaning Devices for Removal Efficiency by Particle Size (see Informative Annex B: Bibliography). Note b: Additional prefilters may be used to reduce maintenance for filters with efficiencies higher than MERV 7. Note c: As an alternative, MERV-14 rated filters may be used in Filter Bank No. 2 if a tertiary terminal HEPA filter is provided for these spaces. Note d: High-Efficiency Particulate Air (HEPA) filters are those filters that remove at least 99.97% of 0.3 micron-sized particles at the rated flow in accordance with the testing methods of IEST RP-CC001.3 (see Informative Annex B, Bibliography). |  | 

## Slide 22: ANSI /ASHRAE /ASHE Standard 170-2008 Table 7-1 Design Parameters— From ANSI/ASHRAE/ASHE Standard 170-2008

## Slide 24: Carbon Filters
1. Are carbon filters really of any value?
2. Where are the best locations and applications for using carbon filters in hospitals?

## Slide 25: CARBON FILTER APPLICATIONS: HOSPITAL

## Slide 26: CARBON FILTER APPLICATIONS: HOSPITAL

## Slide 27: Volcanic Eruption
The most abundant gas typically released into the atmosphere from volcanic systems is water vapor (H2O), followed by carbon dioxide (CO2) and sulfur dioxide (SO2). Volcanoes also release smaller amounts of others gases, including hydrogen sulfide (H2S), hydrogen (H2), carbon monoxide (CO), hydrogen chloride (HCL), hydrogen fluoride (HF), and helium (He).
http://volcanoes.usgs.gov/hazards/gas/

## Slide 28: Filtration Products offered
The carbon needed would be as follows.
carbon dioxide (CO2) - None
sulfur dioxide (SO2) – TS-202
hydrogen sulfide (H2S) – TS-202
hydrogen (H2) – TS-202
carbon monoxide (CO) - None
hydrogen chloride (HCL) – TS-202
hydrogen fluoride (HF) – TS-202
helium (He) - None

## Slide 29: GAS / VAPOR PHASE AIR FILTERS

## Slide 38: QUESTIONS ?